Instructions:

The latest HpmTools_V0024：

To choose “UPS Runtime” and then tool will show “UPS Elapsed time” and “Run time limit”.

- To click “set” and type in password: kstar.

- To set “UPS Elapsed time” in 0 that mean elapsed time be returned to zero.

- Setting “Run time limit” that means to set the pre maintenance alarm for next time alarm. The default value is 30000 hours.

- When meet the “run time limit”, monitoring system will have alarm (five times in a row/ 10mins) and frame will also show ”System need maintanance” on the LCD.