

**Instructions:**


The latest HpmTools\_V0024：

To choose “UPS Runtime” and then tool will show “UPS Elapsed time” and “Run time limit”.







1. To click “set” and type in password: kstar.



1. To set “UPS Elapsed time” in 0 that mean elapsed time be returned to zero.



1. Setting “Run time limit” that means to set the pre maintenance alarm for next time alarm. The default value is 30000 hours.



1. When meet the “run time limit”, monitoring system will have alarm (five times in a row/ 10mins) and frame will also show ”System need maintanance” on the LCD.

